## 2026_Town_Dam_Month-to-Date_Wat
Form Completed By: | Date and Time of Check-In | Hwy 557 Ruler | Dam Ruler (N/A when Logs Out) | Is Water Level In Compliance | OOC Comment | GM Steps to Correct (new) | Weather (temperature in celsius) | Water Management Plan Period | Type of Check-In | Bay 1: TURBINES | Bay 2: 6 Logs Maximum | Bay 3: 8 Logs Maximum | Bay 4: 10 Logs Maximum | Bay 5: MECH GATE MAX 9 Logs | Bay 1 After change: TURBINES | Bay 2 After change: 6 Logs Maximum | Bay 3 after change: 8 Logs Maximum | Bay 4 after change: 10 Logs Maximum | Bay 5 after change: MECH GATE MAX 9 Logs | Dam Ruler After Log Changes | WATER TEMPERATURE if required
Zoran | 2026-06-24 11:55 |  | 0.63 | Yes, but need to provide additional information regarding Water Levels | Forecasting 80% chance of 10mm of rain for tomorrow. |  | 18 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out | 0.63
Zoran | 2026-06-24 09:27 | 0.63 |  | YES |  |  | 18 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Colin | 2026-06-23 14:33 | 63 |  | YES |  |  | 26 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Dana | 2026-06-23 12:17 | .635 (.63-.64) |  | YES |  |  | 22c; 60% chance of 1-3mm Thursday now. | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Zoran | 2026-06-23 11:37 |  | 0.63 | YES |  |  | 22 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out | 0.635
Zoran | 2026-06-23 09:23 | 0.635 |  | YES |  |  | 19 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out
Zoran | 2026-06-22 11:34 |  | 0.64 | Yes, but need to provide additional information regarding Water Levels | Upstream log pull completed today. |  | 22 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 1 Log Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out | 0.635
Zoran | 2026-06-22 09:22 | 0.635 |  | YES |  |  | 18 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1 Log Out
Dana | 2026-06-21 08:37 | Holding .6375-.64 |  | Yes, but need to provide additional information regarding Water Levels | Forecast change has pushed forecasted rain to later in the week (starting Wed). Will continue to target holding between .63-.65 for the start of the week, until closer to forecasted larger rain accumulation, and/or until additional flow from upstream arrives. Will increase checks as needed to track and trend faster changing conditions when needed, drawing down further when needed for flow increases, or forecasted rains increase to include heavy rain especially if after ground saturation. |  | 16C | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1 Log Out
Dana | 2026-06-20 08:08 | .6375-.64 |  | YES |  |  | 9C, sunny | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1 Log Out
Zoran | 2026-06-19 11:47 |  | 0.635 | YES |  |  | 18 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 1 Log Out
Zoran | 2026-06-19 09:17 | 0.645 |  | YES |  |  | 14 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1 Log Out
Jason | 2026-06-18 14:01 |  | 64 | YES |  |  | 17 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | .5 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 1 Log Out | 64
Dana | 2026-06-18 11:40 | .645 (.64-.65) |  | YES |  |  | 16, heavy rain last night | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | .5 Logs Out
Zoran | 2026-06-18 09:14 | .64-.65 |  | YES |  |  | 14 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | .5 Logs Out
Jason | 2026-06-17 12:07 |  | 62 | YES |  |  | 16 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | .5 Logs Out
Zoran | 2026-06-17 09:29 | 0.63 |  | YES |  |  | 15 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | .5 Logs Out
Zoran | 2026-06-16 15:29 | 0.63 |  | YES |  |  | 21 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | .5 Logs Out
Jason | 2026-06-16 11:47 |  | 62 | YES |  |  | 16 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | .5 Logs Out
Jason | 2026-06-16 09:27 | 63 |  | YES |  |  | 16 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | .5 Logs Out
Zoran | 2026-06-15 12:15 |  | 0.62 | YES |  |  | 17 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 1 Log Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | .5 Logs Out | 0.62
Zoran | 2026-06-15 09:45 | 0.62 |  | YES |  |  | 14 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1 Log Out
Colin | 2026-06-14 07:54 |  | 62 | YES |  |  | 14 | Jun. 1 to Sep. 30 | ONSITE only Headpond | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 1 Log Out | 62
Colin | 2026-06-14 07:37 | 62.5 |  | YES |  |  | 12 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Colin | 2026-06-13 07:37 |  | 62.5 | YES |  |  | 15 | Jun. 1 to Sep. 30 | ONSITE only Headpond | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Greg | 2026-06-12 11:29 | 63 |  | YES |  |  | 15 overcast | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 2.5 Logs Out
Dana | 2026-06-12 06:28 | .64 (.635-.645/.65) |  | Yes, but need to provide additional information regarding Water Levels | Drew down as last night and a few nights prior had larger amounts of rain forecasted. Will monitor levels and close mechanical gate as needed to maintain levels in higher end of compliance (compliance range is .60 to .66 for summer, to Sep 30). Once level returns to a decline after rain, we will begin closing gate to hold, which will bring level back up slightly. Only Mechanical gate is spilling water at the dam at this time. |  | 16C, heavier rain just stopped from last night, 40% <-mm this afternoon | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 2.5 Logs Out
Colin | 2026-06-11 15:50 |  | Just shy of 64 | YES |  |  | 24 | Jun. 1 to Sep. 30 | ONSITE only Headpond | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 2.5 Logs Out
Colin | 2026-06-11 14:43 | 64 |  | YES |  |  | 25 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out
Colin | 2026-06-11 11:17 |  | 64 | YES |  |  | 19 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out | 64
Colin | 2026-06-11 09:18 | 64-65 |  | YES |  |  | 19 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Colin | 2026-06-10 12:15 |  | 64.5 | YES |  |  | 25 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Colin | 2026-06-10 09:28 | 64 |  | YES |  |  | 22 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out
Greg | 2026-06-09 11:57 |  | 63 | YES |  |  | 23 sunny | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out
Greg | 2026-06-09 09:22 | 65 |  | YES |  |  | 21 overcast | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out
Greg | 2026-06-08 12:33 |  | 64-64.5 on ruler | YES |  |  | 25 sunny | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out
Zoran | 2026-06-08 09:28 | .645-.65 |  | YES |  |  | 19 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out
Zoran | 2026-06-07 10:31 |  | 0.76 | NO | Over compliance. | Drawing down into top of compliance slowly for increased rain in forecast and anticipated water flow from upstream/ds. | 22 | Jun. 1 to Sep. 30 | ONSITE only Headpond | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 2.5 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out | 0.76
Zoran | 2026-06-07 09:08 | .67-.69(wavy) |  | NO | Over compliance. | Drawing down into top of compliance slowly for increased rain in forecast and anticipated water flow from upstream/ds. | 20 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 2.5 Logs Out
Zoran | 2026-06-06 07:25 | 0.69 |  | NO | Over compliance. | Drawing down into compliance slowly while monitoring rain and upstream water flow/ds. | 17 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 2.5 Logs Out
Greg | 2026-06-05 15:55 | 69-69.5 |  | No, but only 557 checked so far |  |  | 20 overcast misting rain | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 3 Logs Out
Zoran | 2026-06-05 11:00 |  | 0.7 | NO | Over compliance. | Drawing down towards compliance slowly for forecasted rain today and over next 5 days | 19 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 3 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 2.5 Logs Out | 0.7
Zoran | 2026-06-05 09:13 | 0.71 |  | NO | Over compliance. | Drawing down towards compliance slowly for forecasted rain today and over next 5 days. | 17 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 3 Logs Out
Danny | 2026-06-04 15:06 |  | 72-72 1/2 | YES |  |  | 22 | Jun. 1 to Sep. 30 | RULER only Dam |  | 1 Log Out | 1 Log Out | 1 Log Out | 2.5 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 3 Logs Out | 72 72 1/2
Zoran | 2026-06-04 09:10 |  | 0.74 | NO | Over compliance. | Due to dry forecast, to allow it to drop into compliance on its own.As forecast has changed for tomorrow, we will adjust gate today. | 17 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 2.5 Logs Out | 0.735
Zoran | 2026-06-03 11:23 |  | 0.745 | NO | Over compliance. Due to dry forecast, to allow it to drop into compliance on its own. Will monitor and adjust if needed. |  | 26 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Zoran | 2026-06-03 09:37 | 0.75 |  | NO | Over compliance. Due to dry forecast allowing it to drop into compliance on its own. Will monitor and adjust if needed. |  | 21 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Colin | 2026-06-02 11:38 |  | 74 | NO | Do to dry forcast,to allow it to drop into compliance on its own. Will monitor and adjust if needed. |  | 22 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Colin | 2026-06-02 09:14 | 75 |  | NO | Due to dry forcast, to allow it to drop into compliance on its own. Will monitor and adjust if needed. |  | 19 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Colin | 2026-06-01 11:28 |  | 74 | NO | Due to dry forcast,to allow it to drop into compliance on its own. Will monitor and adjust if needed. |  | 20 | Jun. 1 to Sep. 30 | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Colin | 2026-06-01 09:16 | 75 |  | NO | Due to dry forecast, to allow it to drop into compliance on its own. Will monitor and adjust if needed. |  | 19 | Jun. 1 to Sep. 30 | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Dana | 2026-05-30 17:30 | .735 (.73-.75, but settles mostly at .735, same as this AM) |  | NO | Level is in compliance. Just flagging to add additional info. I was going to open the gate slightly to assist with coming into June 1 compliance, but given dry forecast, that Scarfe is closed up, and that the 557 ruler held from this morning, I'll continue to monitor at this time. If level comes up any further I'll open gate at town dam to release a bit more. If it holds, it will likely start to decline on its own and I will permit it to drop into compliance unless forecast changes and we get more rain than currently forecasted. |  | 22C | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Dana | 2026-05-30 09:21 | .74 (.73–.75), will open gate a small amount to assist with decline into compliance change starting tomorrow. Wanted to come in from higher side due to drier forecast and decreased flow from scarfe as Canoe Lake is now recovering to return to compliance now also. Ruler reading to change from yesterday as it was reported at .69 but photo backup showed it was .71 |  | YES |  |  | 13C, in 14-day forecast 60% chance of 1-3mm on June 4th, 60% chance of ~10mm on June 10th. Small % for remaining days from 10-30% chance each day, but no accumulation noted | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Zoran | 2026-05-29 11:59 |  | 0.71 | YES |  |  | 22 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out | [6 empty] | 12
Zoran | 2026-05-29 09:23 | 0.69 |  | YES |  |  | 17 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out
Greg | 2026-05-28 11:44 |  | 69 | YES |  |  | 14 sunny | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | NO LOGS OUT = Both Off | 1 Log Out | 1 Log Out | 2 Logs Out | 2 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 1.5 Logs Out |  | N/A
Zoran | 2026-05-28 09:19 | .68-.69 |  | YES |  |  | 15 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out
Colin | 2026-05-27 09:36 |  | 60 | YES |  |  | 18 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 1 Log Out | 1 Log Out | 1 Log Out | 5 Logs Out | Both OFF = NO LOGS OUT | 1 Log Out | 1 Log Out | 1 Log Out | 2 Logs Out | 61 | 14
Dana | 2026-05-27 06:47 | 0.645 |  | NO | In compliance. Flagged to add notes. Will closing gate further today and sealing bays for summer hold. This should level out the water level between dam and 557 rulers, and let it come up a small amount so it is at or close to summer hold max compliance level due for June 1st of .66. |  | 7C, no rain in next 7 days forecasted | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 5 Logs Out
Colin | 2026-05-26 10:49 | Wavy moving 64-66 |  | YES |  |  | 18 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 1 Log Out | 1 Log Out | 1 Log Out | 5 Logs Out
Colin | 2026-05-26 09:27 |  | 58-59 | YES |  |  | 18 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4 Logs Out | #2 ON only = 2 Logs Out | 1 Log Out | 1 Log Out | 1 Log Out | 5 Logs Out | 60 | 14
Colin | 2026-05-25 16:03 |  | 59 | YES |  |  | 19 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4.5 Logs Out | #2 ON only = 2 Logs Out | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4 Logs Out | 59 | 12
Colin | 2026-05-25 15:46 | 66 |  | YES |  |  | 19 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4.5 Logs Out
Zoran | 2026-05-25 11:21 |  | 0.58 | YES |  |  | 14 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4.5 Logs Out | [6 empty] | 12
Zoran | 2026-05-25 09:12 | 0.665 |  | YES |  |  | 12 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 2 Logs Out | 2 Logs Out | 4 Logs Out | 4.5 Logs Out
Zoran | 2026-05-20 09:11 | 0.59 |  | NO | Level declining as we prepare to drop more logs in batches and prep for summer hold. Level will come up again after each group of drops, reducing the taper to the dam sill and working to level out the river as we return more logs to their bay. As water declines again we will complete next batch of drops and continue in this manner until all logs are returned to the dam, unless we need to keep a minimal amount out to maintain summer hold levels, etc. |  | 8 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 5 Logs Out
Zoran | 2026-05-19 09:08 | .61-.615 |  | YES |  |  | 13 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX)
Zoran | 2026-05-15 14:40 | 0.61 |  | YES |  |  | 14 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX)
Zoran | 2026-05-15 09:38 | .61-.62 |  | YES |  |  | 13 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX)
Colin | 2026-05-14 11:23 |  | Moving 8-14 | YES |  |  | 16 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX) | [6 empty] | 7
Colin | 2026-05-13 11:40 |  | 2026-08-15 | YES |  |  | 8 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX) | [6 empty] | 7
Colin | 2026-05-12 15:14 |  | Moving 9-13 | YES |  |  | 8 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX) | [6 empty] | 7
Zoran | 2026-05-12 11:19 | 0.67 |  | YES |  |  | 10 | Apr. 1 to May 31 *Take Water Temp* | RULER only 557 bridge |  | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX)
Colin | 2026-05-11 15:12 |  | Moving 0-9 | YES |  |  | 9 | Apr. 1 to May 31 *Take Water Temp* | ONSITE both Headpond & Powerhouse | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 10 Logs Out (MAX) | 4 Logs Out | #2 ON only = 2 Logs Out | 6 Logs Out (MAX) | 8 Logs Out (MAX) | 4 Logs Out | 9 Logs Out (MAX) | Moving 12-20 | 7