## 2025_Town_Dam_Month-to-Date_Wat
Form Completed By: | Date and Time of Check-In | Type of Check-In | Hwy 557 Ruler | Dam Ruler (N/A when Logs Out) | Is Water Level In Compliance | Which Ruler is in Compliance? | Weather (temperature in celsius) | WATER TEMPERATURE if required | Water Management Plan Period | Bay 1: TURBINES | Bay 2: 6 Logs Maximum | Bay 3: 8 Logs Maximum | Bay 4: 10 Logs Maximum | Bay 5: MECH GATE MAX 9 Logs | Bay 1 After change: TURBINES | Bay 2 After change: 6 Logs Maximum | Bay 3 after change: 8 Logs Maximum | Bay 4 after change: 10 Logs Maximum | Bay 5 after change: MECH GATE MAX 9 Logs | OOC Comment | Dam Ruler After Log Changes
Colin | 2026-03-31 14:12 | ONSITE both Headpond & Powerhouse |  | 45 | NO |  | 2 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 3 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | Both OFF = NO LOGS OUT | 3 Logs Out | 3 Logs Out | 3 Logs Out | 6.5 Logs Out | Prepping for freshet and up coming rain.
Colin | 2026-03-31 13:49 | RULER only 557 bridge | 53 |  | NO |  | 2 |  | Feb. 1 to Mar. 31 |  | 3 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | [5 empty] | Prep for freshet
Colin | 2026-03-31 09:25 | RULER only 557 bridge | 53 |  | NO |  | 4 |  | Feb. 1 to Mar. 31 |  | 3 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | [5 empty] | Prep for freshet. No action at this time.
Colin | 2026-03-30 14:20 | RULER only 557 bridge | 53 |  | NO |  | 10 |  | Feb. 1 to Mar. 31 |  | 3 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | [5 empty] | Getting ready for freshet. No action at this time.
Colin | 2026-03-30 13:28 | ONSITE both Headpond & Powerhouse |  | 43 | NO |  | 9 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6 Logs Out | Both OFF = NO LOGS OUT | 3 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | Freshet , will adjust accordingly | 43
Colin | 2026-03-30 09:14 | RULER only 557 bridge | 53 |  | NO |  | 2 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6 Logs Out | [5 empty] | Freshet prep no action at this time.
Zoran | 2026-03-29 11:21 | ONSITE only Headpond |  | 0.51 | NO |  | 2 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 4.5 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6 Logs Out | Under compliance. Prepping for freshet. | 0.49
Zoran | 2026-03-29 11:09 | RULER only 557 bridge | 0.57 |  | NO |  | 2 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 4.5 Logs Out | [5 empty] | Under compliance. Prepping for freshet.
Zoran | 2026-03-28 09:48 | RULER only 557 bridge | 0.555 |  | NO |  | -6 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 4.5 Logs Out | [5 empty] | Under compliance. Prepping for freshet. Monitoring weather forecast.
Zoran | 2026-03-27 11:06 | ONSITE both Headpond & Powerhouse |  | 0.45 | NO |  | -8 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 4.5 Logs Out | Under compliance. Prepping for freshet. | 0.46
Zoran | 2026-03-27 09:26 | RULER only 557 bridge | 0.535 |  | NO |  | -12 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | [5 empty] | Under compliance. Prepping for freshet.
Dana | 2026-03-26 16:09 | RULER only 557 bridge | .53 (.52-.54, settles most at .53, log pulled upstream |  | NO |  | -1C, windy |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | [5 empty] | Freshet prep, log pulled upstream
Colin | 2026-03-26 12:48 | ONSITE both Headpond & Powerhouse |  | 45-46 | NO |  | 4 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | [5 empty] | Water coming up slowly
Zoran | 2026-03-26 09:59 | RULER only 557 bridge | 0.53 |  | NO |  | 2 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | [5 empty] | Under compliance. Prepping for freshet.
Zoran | 2026-03-25 11:01 | ONSITE both Headpond & Powerhouse |  | 0.45 | NO |  | -2 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | [5 empty] | Under compliance. Prep for the freshet.
Greg | 2026-03-25 09:08 | RULER only 557 bridge | 51 |  | No, but only 557 checked so far |  | -3 overcast |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out
Zoran | 2026-03-24 16:01 | ONSITE only Headpond |  | 0.42 | NO |  | 5 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5.5 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | Under compliance. Prepping for freshet. | 0.425
Zoran | 2026-03-24 15:48 | RULER only 557 bridge | 0.5 |  | NO |  | 6 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5.5 Logs Out | [5 empty] | Under compliance. Prep for freshet.
Zoran | 2026-03-24 10:36 | ONSITE both Headpond & Powerhouse |  | 0.415 | NO |  | -2 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5.5 Logs Out | [5 empty] | Under compliance. Prep for freshet.
Greg | 2026-03-24 09:26 | RULER only 557 bridge | 50 |  | NO |  | -4 snowing |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5.5 Logs Out | [5 empty] | Freshet prep
Colin | 2026-03-23 12:01 | RULER only 557 bridge | 49 |  | NO |  | -3 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5.5 Logs Out | [5 empty] | No action yet we will wait until it comes up a bit
Zoran | 2026-03-23 10:29 | ONSITE both Headpond & Powerhouse |  | 0.38 | NO |  | -3 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6.5 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5.5 Logs Out | Under compliance due to expected water from upstream. | 0.39
Colin | 2026-03-23 09:29 | RULER only 557 bridge | 49 |  | NO |  | -4 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6.5 Logs Out | [5 empty] | Will close gate a bit today
Zoran | 2026-03-20 12:08 | ONSITE both Headpond & Powerhouse |  | 0.38 | NO |  | 4 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 7 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6.5 Logs Out | Under compliance. Perp for freshet and incoming water from upstream. | 0.39
Colin | 2026-03-20 09:43 | RULER only 557 bridge | 54 |  | NO |  | -1 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 7 Logs Out | [5 empty] | No action yet . Prepping for freshete and incoming water.
Zoran | 2026-03-19 15:45 | ONSITE both Headpond & Powerhouse |  | 0.42 | NO |  | 4 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6.5 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 7 Logs Out | Under compliance. Prep for freshet and incoming water from upstream. | 0.405
Zoran | 2026-03-19 14:49 | RULER only 557 bridge | 0.59 |  | NO |  | 4 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6.5 Logs Out | [5 empty] | Under compliance. Prepping for freshet and incoming water from upstream.
Colin | 2026-03-18 10:58 | ONSITE both Headpond & Powerhouse |  | 45-46 | NO |  | -11 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6.5 Logs Out | [5 empty] | Drawn down for upcoming weather and spring thaw.
Colin | 2026-03-18 09:30 | RULER only 557 bridge | 58-59 |  | NO |  | -12 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6.5 Logs Out | [5 empty] | Letting draw down . No adjustment today. MNR aware
Colin | 2026-03-17 13:34 | RULER only 557 bridge | 59-60 |  | NO |  | -5 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6.5 Logs Out | [5 empty] | No action yet
Colin | 2026-03-15 08:06 | RULER only 557 bridge | 58-59 |  | NO |  | -5 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6.5 Logs Out | [5 empty] | Will continue to drawn down for up coming weather.
Colin | 2026-03-14 09:36 | ONSITE both Headpond & Powerhouse |  | 52 | YES | 557 ruler | -8 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6.5 Logs Out
Colin | 2026-03-14 09:34 | RULER only 557 bridge | 60.5 |  | YES | 557 ruler | -8 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out
Greg | 2026-03-13 13:22 | ONSITE both Headpond & Powerhouse |  | 49.5-50 | NO |  | -3 heavy winds and blowing snow |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 4.5 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | Opened mechanical gate and lots of precipitation rain and snow in close forecast. Chipped ice and salted at powerhouse entrance, returned mechanical gate disconnect to off position after adjustment.
Colin | 2026-03-13 09:25 | RULER only 557 bridge | 59 |  | NO |  | -4 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 4.5 Logs Out | [5 empty] | Closed mechanical gate yesterday level is coming up slowly
Colin | 2026-03-12 15:54 | RULER only 557 bridge | 57 |  | NO |  | 0 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 4.5 Logs Out | [5 empty] | We closed mechanical gate a bit
Dana | 2026-03-12 14:41 | ONSITE both Headpond & Powerhouse |  | 0.5 | NO |  | -3C, sunny |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 4.5 Logs Out | [5 empty] | Freshet prep staying low
Greg | 2026-03-12 13:03 | ONSITE both Headpond & Powerhouse |  | 48-49 | NO |  | 2 sunny |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 4.5 Logs Out | Recent rain and warm weather will help with levels, snow in forecast and will adjust gate. Water is on its way from above.
Colin | 2026-03-12 09:30 | RULER only 557 bridge | 57 |  | NO |  | -6 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6 Logs Out | [5 empty] | We will close gate. Amount depending on upstream.
Greg | 2026-03-11 13:30 | ONSITE both Headpond & Powerhouse |  | 56-57 | NO |  | -1 overcast and periods of freezing rain |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 7 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6 Logs Out | Adjusted gate and heavy precipitation in forecast.
Colin | 2026-03-11 09:40 | RULER only 557 bridge | 59 |  | NO |  | -1 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 7 Logs Out | [5 empty] | opened dam to pass water from early thaw period before dropping in temp again. Flow declined in basin before receiving increased flow from upstream release, but given the amount of snow/ice to melt this year, will be trying to stay at bottom or slightly under compliance. Starting freshet below compliance is the only way we will be able to pass the water without going too far over compliance given the tight range and that there is no spill wall for the Town Dam and no secondary outlet to Huron. /ds
Colin | 2026-03-10 16:01 | ONSITE only Headpond |  | 50 | YES | 557 ruler | 2 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 7 Logs Out |  | 49
Colin | 2026-03-10 15:34 | RULER only 557 bridge | 62 |  | YES | 557 ruler | 1 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6 Logs Out
Colin | 2026-03-10 11:58 | ONSITE both Headpond & Powerhouse |  | 57 | YES | 557 ruler | 4 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 6 Logs Out |  | 57
Colin | 2026-03-10 09:17 | RULER only 557 bridge | 62 |  | YES | 557 is, Town Dam not checked yet | 1 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out
Colin | 2026-03-09 15:42 | RULER only 557 bridge | 61 |  | YES | 557 ruler | 13 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out
Colin | 2026-03-09 13:41 | ONSITE both Headpond & Powerhouse |  | 57 | YES | 557 ruler | 11 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 4 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 5 Logs Out
Colin | 2026-03-09 09:36 | RULER only 557 bridge | 61 |  | YES | 557 is, Town Dam not checked yet | 5 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 4 Logs Out
Zoran | 2026-03-08 09:35 | ONSITE only Headpond |  | 0.55 | YES | 557 ruler | 1 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 3.5 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 4 Logs Out |  | 0.55
Zoran | 2026-03-08 09:18 | RULER only 557 bridge | 0.6 |  | YES | 557 ruler | 1 |  | Dec. 1 to Dec. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 3.5 Logs Out
Zoran | 2026-03-07 09:47 | ONSITE only Headpond |  | 0.55 | NO |  | 3 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 3 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 3.5 Logs Out | Under compliance. Ok to remain under compliance because of the warm weather and forecasted rain. | 0.55
Zoran | 2026-03-07 07:14 | RULER only 557 bridge | 0.58 |  | NO |  | 3 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 3 Logs Out | [5 empty] | Under compliance. Remaining under compliance due to warm weather and upcoming weather forecast(rain).
Zoran | 2026-03-06 13:58 | ONSITE both Headpond & Powerhouse |  | 0.55 | NO |  | 1 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 2.5 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 3 Logs Out | Under compliance. Ok to remain below compliance due to warm weather and forecasted rain. | 0.55
Zoran | 2026-03-06 12:28 | RULER only 557 bridge | 0.575 |  | NO |  | 1 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 2.5 Logs Out | [5 empty] | Ok to remain under compliance due to warm weather and forecasted rain.
Greg | 2026-03-05 13:13 | ONSITE only Headpond |  | 56 | NO |  | 6 sunny |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 2.5 Logs Out | [5 empty] | 15-20 mm or rain expected and very warm temperatures to help with levels.
Colin | 2026-03-04 12:44 | ONSITE both Headpond & Powerhouse |  | 57 | NO |  | 5 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 2 Logs Out | Both OFF = NO LOGS OUT | 2 Logs Out | 3 Logs Out | 3 Logs Out | 2.5 Logs Out | Low water
Colin | 2026-03-04 09:32 | RULER only 557 bridge | 59 |  | NO |  | 2 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 2 Logs Out | [5 empty] | No action. Rain and mild temps expected.
Colin | 2026-03-03 13:35 | ONSITE both Headpond & Powerhouse |  | 57 | NO |  | -1 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 2 Logs Out | [5 empty] | No action today because of forecasted rain and mild weather.
Colin | 2026-03-03 09:32 | RULER only 557 bridge | 59 |  | NO |  | -3 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 2 Logs Out | [5 empty] | No action because of forecasted rain and mild temps voming.
Colin | 2026-03-02 12:50 | ONSITE both Headpond & Powerhouse |  | 57 | YES | 557 ruler | -3 |  | Feb. 1 to Mar. 31 | NO LOGS OUT = Both Off | 2 Logs Out | 3 Logs Out | 3 Logs Out | 2 Logs Out
Colin | 2026-03-02 09:38 | RULER only 557 bridge | 60 |  | YES | 557 is, Town Dam not checked yet | -11 |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 2 Logs Out
Dana | 2026-03-01 09:19 | RULER only 557 bridge | 0.605 |  | YES | 557 is, Town Dam not checked yet | -20C |  | Feb. 1 to Mar. 31 |  | 2 Logs Out | 3 Logs Out | 3 Logs Out | 2 Logs Out